This product has received a verified Environmental Product Declaration (EPD) based on a North American Product Category Rule (PCR.)

SECTION 08 71 13

AUTOMATIC DOOR OPERATORS

Specifier Note: This specification document shall serve as a guide specification for typical projects where the Stanley Access Technologies Magic-Access, low energy, automatic door operator will be the basis of design. Specification must be reviewed for applicability on a per project basis. The specifier is directed to select appropriate options included herein. Consult with the local Access Technologies Territory Manager, when options, not specified, are required. See last page of this document for a summary of unspecified options.

- GENERAL

  - RELATED DOCUMENTS

    - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

  - SUMMARY

    - This Section includes the following types of automatic door operators:

      - Exterior and interior, automatic door operators, low energy, with visible mounting.

      - Automatic door operators shall be configured for doors as follows:

        - Simultaneous pairs, out swing, in swing, or double egress.

        - Simultaneous pairs, with single operator, out swing or in swing.

        - Single doors, out swing or in swing.

    - Related Sections:

      - Division 8 Section “Doors and Frames” for entrances furnished separately in Division 8 Section.

      - Division 8 Section "Aluminum-Framed Entrances and Storefronts" for entrances furnished separately in Division 8 Section.

      - Division 8 Section "Door Hardware" for hardware to the extent not specified in this Section.

      - Division 26 Sections for electrical connections including conduit and wiring for power to, and control of, automatic door operators.

  - REFERENCES

    - General: Standards listed by reference, including revisions by issuing authority, form a part of this specification section to extent indicated. Standards listed are identified by issuing authority, authority abbreviation, designation number, title or other designation established by issuing authority.  Standards subsequently referenced herein are referred to by issuing authority abbreviation and standard designation.

    - Underwriters Laboratories (UL):

      - UL 325 – Standard for Door, Drapery, Gate, Louver, and Window Operators and Systems.

      - UL 10C – Positive Pressure Fire Tests of Door Assemblies

    - American National Standards Institute (ANSI)/Builders’ Hardware Manufacturers Association (BHMA):

      - ANSI/BHMA A156.19: Standard for Power Assist and Low Energy Power Operated Doors.

    - American Society for Testing and Materials (ASTM):

      - ASTM B221 - Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

      - ASTM B209 - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

    - American Association of Automatic Door Manufacturers (AAADM):

    - International Code Council (ICC):

      - IBC: International Building Code

    - Building Officials and Code Administrators International (BOCA), 1999:

    - National Fire Protection Association (NFPA):

      - NFPA 101 – Life Safety Code.

      - NFPA 70 – National Electric Code.

    - International Standards Organization (ISO):

      - ISO 9001 - Standard for Manufacturing Quality Management Systems

      - ISO 14025 – Environmental Labels and Declarations -- Type III Environmental Declarations -- Principles and Procedures

      - ISO14040 – Environmental Management -- Life Cycle Assessment -- Principles and Framework

      - ISO 14044 – Environmental Management -- Life Cycle Assessment -- Requirements and Guidelines

      - ISO 21930 – Sustainability in Buildings and Civil Engineering Works -- Core Rules For Environmental Product Declarations Of Construction Products And Services

    - National Association of Architectural Metal Manufacturers (NAAMM):

      - Metal Finishes Manual for Architectural and Metal Products.

Specifier Note: Modify paragraph below to suit project requirements. Select appropriate standard finish from options below. Make multiple selections as required; schedule accordingly. See last page of this document for a summary of unspecified finish options. Coordinate with other sections.

    - American Architectural Manufacturers Association (AAMA):

      - [AAMA 606.1 – Integral Color Anodic Finishes for Architectural Aluminum.]

      - [AAMA 607.1 - Clear Anodic Finishes for Architectural Aluminum.]

      - AAMA 611 Voluntary Specification for Anodized Architectural Aluminum.

    - United Nations Central Product Classification (UNCPC):

      - UNCPC 4212 - Product Category Rules for Preparing an Environmental Product Declaration for Power-Operated Pedestrian Doors and Revolving Doors

  - DEFINITIONS

    - Activation Device:  Device that, when actuated, sends an electrical signal to the door operator to open the door.

  - PERFORMANCE REQUIREMENTS

    - Provide automatic door operators capable of withstanding structural loads and thermal movements based on testing manufacturer's standard units in assemblies similar to those indicated for this Project.

    - Operating Range:  Minus 30 deg F (29 deg C) to 130 deg F (54 deg C).

    - Opening-Force Requirements for Egress Doors: In the event power failure to the operator, swinging automatic entrance doors shall open with a manual force, not to exceed 30 lbf (133 N) to set door in motion, and not more than 15 lbf to fully open the door. Forces shall be applied at 1” (25 mm) from the latch edge of the door.

    - Break Away Requirements: Automatic door operators provided with a breakaway device shall require no more than 50 lbf (222 N) applied at 1” (25 mm) from the latch edge of the door.

  - SUBMITTALS

    - Submit listed submittals in accordance with Conditions of the Contract and Division 01 submittal procedures.

    - Shop Drawings:  Include plans, elevations, sections, details, hardware mounting heights, and attachments to other work. Indicate wiring for electrical supply.

    - Color Samples for selection of factory-applied color finishes.

    - Closeout Submittals: Provide the following with project close-out documents.

      - Owner’s Manual.

      - Warranties.

    - Reports:  Based on evaluation performed by a qualified agency, for automatic door operators.

      - Environmental Product Declaration.

      - Evaluation Report for compliance with IBC.

  - QUALITY ASSURANCE

    - Installer Qualifications:  Manufacturer's authorized representative, with certificate issued by AAADM, who is trained for installation and maintenance of units required for this Project.

    - Manufacturer Qualifications:  A qualified manufacturer with a manufacturing facility certified under ISO 9001.

    - Manufacturer shall have in place a national service dispatch center providing 24 hours a day, 7 days a week, emergency call back service.

    - Certifications: Automatic door operators shall be certified by the manufacturer to meet performance design criteria in accordance with the following standards:

      - ANSI/BHMA A156.19.

      - NFPA 101.

      - UL 325 Listed.

      - UL 10C Listed.

      - IBC 2009 and 2012.

      - BOCA.

    - Environmental Product Declaration (EPD): EPD for automatic door operators shall be certified by the manufacturer to comply with the following:

      - Prepared under Product Category Rule (PCR) UNCPC 4212.

      - Conform to ISO standards 14025, 14040, 14044, 21930

      - Life Cycle Assessment Basis: Cradle to Gate, minimum.

    - Source Limitations:  Obtain automatic door operators through one source from a single manufacturer.

    - Product Options:  Drawings indicate sizes, profiles, and dimensional requirements of automatic entrance door assemblies and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

    - Power Operated Door Standard: ANSI/BHMA A156.19.

    - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

    - Emergency-Exit Door Requirements:  Comply with requirements of authorities having jurisdiction for swinging automatic entrance doors serving as a required means of egress.

  - PROJECT CONDITIONS

    - Field Measurements:  General Contractor shall verify openings to receive automatic door operators by field measurements before fabrication and indicate measurements on Shop Drawings.

    - Mounting Surfaces:  General Contractor shall verify all surfaces to be plumb, straight and secure; substrates to be of proper dimension and material.

    - Other trades:  General Contractor Advise of any inadequate conditions or equipment.

  - COORDINATION

    - Templates:  Check Shop Drawings of other work to confirm that adequate provisions are made for locating and installing automatic door operators to comply with indicated requirements.

    - Electrical System Roughing-in: Coordinate layout and installation of automatic door operators with connections to, power supplies, remote activation devices, and electric door latching hardware.

    - System Integration: Integrate automatic door operators with other systems as required for a complete working installation. Where required for proper operation, provide a time delay relay to signal automatic door operator to activate only after electric lock system is released.

  - WARRANTY

    - Automatic door operators shall be free of defects in material and workmanship for a period of one (1) year from the date of substantial completion.

    - During the warranty period the Owner shall engage a factory-trained technician to perform service and affect repairs. A safety inspection shall be performed after each adjustment or repair and a completed inspection form shall be submitted to the Owner.

    - During the warranty period all warranty work, including but not limited to emergency service, shall be performed during normal working hours.

- PRODUCTS

  - AUTOMATIC DOOR OPERATORS

    - Manufacturer: Stanley Access Technologies; Magic-Access™ Series automatic door operator.

  - MATERIALS

    - Aluminum:  Alloy and temper recommended by manufacturer for type of use and finish indicated.

      - Headers: 6063-T6.

      - Extruded Bars, Rods, Profiles, and Tubes:  ASTM B 221.

      - Sheet and Plate:  ASTM B 209.

    - Sealants and Joint Fillers:  Refer to Division 7 Section "Joint Sealants".

  - COMPONENTS

    - Header Case: Header case shall not exceed 6-1/8 inch x 4 inch (156 mm x 102 mm) in rectangular section and shall be fabricated from extruded aluminum with structurally integrated end caps, designed to conceal door operators and controls. The operator shall be sealed against dust, dirt, and corrosion within the header case. Access to the operator and electronic control box shall be provided by a full-length removable cover, edge rabbetted to the header to ensure a flush fit.  Removable cover shall be secured to prevent unauthorized access.

    - Door Arms and Linkage Assembly: A combination of door arms and linkage shall provide positive control of door through entire swing; units shall permit use of butt hung, center pivot, and offset pivot-hung doors.

    - Fasteners and Accessories:  Manufacturer's standard corrosion-resistant, non-staining, non-bleeding fasteners and accessories compatible with adjacent materials.

    - Signage:  Provide signage in accordance with ANSI/BHMA A156.19.

  - SWINGING DOOR OPERATORS

    - General:  Provide door operators of size recommended by manufacturer for door size, weight, and movement; for condition of exposure; and for long-term, maintenance-free operation under normal traffic load for type of occupancy indicated.

    - Operators:  Self-contained units powered by a minimum fractional horsepower, permanent-magnet DC motors.

      - Electro-mechanical Operator: Transmit power from operator to door through reduction gear train, splined spindle, door arm, and linkage assembly.  Drive train shall have positive constant engagement.

      - Operation:  Power opening and spring closing.

      - Capacity: Rated for door panels weighing up to 125 lb (57 kg)

      - Mounting: Visible

      - Features:

        - Adjustable opening, open check, and closing speeds.

        - Adjustable opening force.

        - Adjustable hold-open time between 0 and 30 seconds.

        - Reverse on obstruction.

        - Push to operate activation.

    - Closing Operation: The operator shall close the door by spring energy employing the motor, as a dynamic brake to provide closing speed control. The closing spring shall be adjustable for positive closing action at a low material stress level for long spring life.

    - Manual Use: The operator shall function as a manual door closer in the direction of swing with or without electrical power. The operator shall deliver an even, consistent open force across the entire transition from door fully closed to door fully open.

    - Electrical service to door operators shall be provided under Division 26 Electrical.  Minimum service to be 120 VAC, 5 amps.

  - ELECTRICAL CONTROLS

    - Electrical Control System: Electrical control system shall include a solid state controller with quick connect plugs.

    - Controller Protection: The controller shall incorporate the following features to ensure trouble free operation:

      - Main Fuse Protection.

      - Electronic Surge Protection.

      - Internal Power Supply Protection.

      - Motor Protection, over-current protection.

    - Program Dip Switches: The controller shall have program dip switches to allow selection or change of activation options; standard activation or push-to-operate.

    - Power Switch: Automatic door operators shall be equipped with a two position On/Off switch to control power to the door.

  - ACTIVATION DEVICES

    - Push Plates: Provide 4 ½ inch (114 mm) square SPDT push plates with UL listed switch.  Face plates and mounting studs shall be stainless steel.  Face plates shall be engraved with the international symbol for accessibility and “Push To Open”. Push plates shall be wall mounted in single or double gang electrical boxes and hardwired to door operator controls.

  - ALUMINUM FINISHES

    - Comply with NAAMM Metal Finishes Manual for Architectural and Metal Products for recommendations for applying and designing finishes. Finish designations prefixed by AA comply with system established by Aluminum Association for designing finishes.

Specifier Note: Modify paragraph below to suit project requirements. Select appropriate standard finish from options below. Make multiple selections as required; schedule accordingly. See last page of this document for a summary of unspecified finish options.

    - [Class II, Clear Anodic Finish: AA-M12C22A31 Mechanical Finish: as fabricated; Chemical Finish: etched, medium matte; Anodic Coating: Architectural Class II, clear coating 0.40 mils minimum complying with AAMA 611-98, and the following:

      - AAMA 607.1

      - Applicator must be fully compliant with all applicable environmental regulations and permits, including wastewater and heavy metal discharge.]

    - [Class I, Color Anodic Finish: AA-M12C22A42/A44 Mechanical Finish: as fabricated; Chemical Finish: etched, medium matte; Anodic Coating: Architectural Class I, integrally colored or electrolytically deposited color coating 0.70 mils minimum complying with AAMA 611-98, and the following:

      - Color: Dark Bronze.

      - AAMA 606.1

      - Applicator must be fully compliant with all applicable environmental regulations and permits, including wastewater and heavy metal discharge.]

- EXECUTION

  - INSPECTION

    - Examine conditions, with Installer present, for compliance with requirements for installation tolerances, header support, and other conditions affecting performance of swinging automatic entrance doors. Proceed with installation only after unsatisfactory conditions have been corrected.

  - INSTALLATION

    - Do not install damaged components.  Fit joints to produce hairline joints free of burrs and distortion. Rigidly secure non-movement joints.

    - Mounting:  Install automatic door operators/headers plumb and true in alignment with established lines and grades.  Anchor securely in place.

      - Install surface-mounted hardware using concealed fasteners to greatest extent possible.

      - Set headers, arms and linkages level and true to location with anchorage for permanent support.

    - Door Operators:  Connect door operators to electrical power distribution system as specified in Division 26 Sections.

  - FIELD QUALITY CONTROL

    - Testing Services:  Factory Trained Installer shall test and inspect each swinging automatic entrance door to determine compliance of installed systems with applicable ANSI standards.

  - ADJUSTING

    - Adjust door operators, controls, and hardware for smooth and safe operation, for tight closure, and complying with requirements in ANSI A156.19 by AAADM Certified Technician.

  - CLEANING AND PROTECTION

    - Clean surfaces promptly after installation.  Remove excess sealant compounds, dirt, and other substances.  Repair damaged finish to match original finish.

END OF SECTION 08 71 13

# Text boxes

Available options not specified in this document are summarized as follows:

- Mounting options (Visible Specified)

  - Concealed; optional with center pivot doors by others.

- Finish options (Standard Options Specified):

  - Color anodizing options; “Champagne” to “Black”

  - Multi-coat Fluoropolymer painted finishes.

  - Cladding.

- Activation options (Standard Hard Wired Push Plates Specified) including:

  - Wireless push plates.

  - Wireless transmitters.

  - Push plate posts.

  - Push to operate.

- Safety options (None Specified) including:

  - Overhead safety systems.

Contact your local Stanley Access Technologies representative for more information on specifying the right sliding automatic entrance for your project.

These specifications represent a “sample” configuration and depict design features that are commonly used. These specifications do not reflect “standard” features and are provided for informational purposes only. Please note that there is no standard “off the shelf” product.  Stanley custom manufactures each product to its customers’ specifications. It is the customer’s responsibility to validate that a particular configuration of Stanley’s products is suitable for a specific application.  All specifications and designs contained herein are subject to change without notice or obligation.