SECTION 08 42 43

INTENSIVE CARE UNIT/CRITICAL CARE UNIT ENTRANCES

Specifier Note: This specification document shall serve as a guide specification for typical projects where the Stanley Access Technologies Dura-Care 7400 Series ICU/CCU entrance will be the basis of design. Specification must be reviewed for applicability on a per project basis. The specifier is directed to select appropriate options included herein. Consult with the local Access Technologies Territory Manager, when options, not specified, are required. See last page of this document for a summary of unspecified options.

- GENERAL

  - RELATED DOCUMENTS

    - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

  - SUMMARY

    - This Section includes the following types of intensive care unit/critical care unit (ICU/CCU) entrances:

      - Interior, manual swinging ICU/CCU entrances.

      - Entrances shall be rated as an effective barrier limiting the passage of smoke.

      - Manual swinging ICU/CCU entrances shall be configured as follows:

        - Simultaneous pairs.

        - Simultaneous pairs, uneven.

        - Single doors.

    - Related Sections:

      - Division 7 Sections for caulking to the extent not specified in this section.

      - Division 8 Section "Door Hardware" for hardware to the extent not specified in this Section.

      - Division 8 Section Glazing for materials and installation requirements of glazing for ICU/CCU entrances.

      - Division 26 Sections for electrical connections including conduit and wiring for grounding of ICU/CCU entrances.

  - REFERENCES

    - General: Standards listed by reference, including revisions by issuing authority, form a part of this specification section to extent indicated. Standards listed are identified by issuing authority, authority abbreviation, designation number, title or other designation established by issuing authority.  Standards subsequently referenced herein are referred to by issuing authority abbreviation and standard designation.

    - American Society for Testing and Materials (ASTM):

      - ASTM B221 - Standard Specification for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

      - ASTM B209 - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

    - International Organization for Standardization (ISO):

      - ISO 9001 - Quality Management Systems

    - National Fire Protection Association (NFPA):

      - NFPA 105 – Standard for the Installation of Smoke Door Assemblies

    - Underwriters Laboratories (UL):

      - UL 1784 – Air Leakage Tests for Door Assemblies

    - International Building Code (IBC) 2003

    - National Association of Architectural Metal Manufacturers (NAAMM):

      - Metal Finishes Manual for Architectural and Metal Products.

    - American Architectural Manufacturers Association (AAMA):

      - AAMA 607.1 - Clear Anodic Finishes for Architectural Aluminum.

      - AAMA 611 Voluntary Specification for Anodized Architectural Aluminum.

      - AAMA 701 Voluntary Specification for Pile Weatherstripping and Replaceable Fenestration Weatherseals.

  - PERFORMANCE REQUIREMENTS

    - Provide ICU/CCU entrances capable of withstanding structural loads and thermal movements based on testing manufacturer's standard units in assemblies similar to those indicated for this Project.

    - Operating Range:  Minus 30 deg F (Minus 34 deg C) to 130 deg F (54 deg C).

    - Opening-Force Requirements for Egress Doors: Not more than 50 lbf (222 N) required to manually set door in motion, and not more than 15 lbf (67 N) required to open door to minimum required width.

    - Smoke and Draft Control: Provide smoke and draft control system on ICU/CCU entrances.  Smoke and draft control system shall provide an effective barrier for limiting the passage of smoke. Smoke and draft control system shall comply with the following:

      - Air Leakage Rates: The maximum air leakage rate for ICU/CCU entrances shall be as follows:

        - Tested without bottom sweep, at 0.10 in water column (25 Pa), leakage shall be less than 3.0 ft3/min/ft2 (0.9 m3/min/m2) of framed opening at ambient temperature; and, less than 1.0 ft3/min/ft2 (0.3 m3/min/m2) of framed opening at elevated temperature.

        - Tested with bottom sweep, at 0.30 in water column (75 Pa), leakage shall be less than 2.5 ft3/min/ft2 (0.8 m3/min/m2) of framed opening at ambient temperature; and, less than 1.0 ft3/min/ft2 (0.3 m3/min/m2) of framed opening at elevated temperature.

      - Door shall be tested in accordance UL 1784.

      - Installation shall be in accordance with NFPA 105.

      - All testing and ratings shall be without artificial bottom seal.

  - SUBMITTALS

    - Submit listed submittals in accordance with Conditions of the Contract and Division 1 Specification Sections.

    - Shop Drawings:  Include plans, elevations, sections, details, hardware mounting heights, and attachments to other work.

    - Color Samples for selection of factory-applied color finishes.

    - Closeout Submittals:

      - Owner’s Manual.

      - Warranties.

  - QUALITY ASSURANCE

    - Installer Qualifications:  Manufacturer's authorized representative, with certificate issued by AAADM, who is trained for installation and maintenance of units required for this Project.

    - Manufacturer Qualifications:  A qualified manufacturer with a manufacturing facility certified under ISO 9001.

    - Manufacturer shall have in place a national service dispatch center providing 24 hours a day, 7 days a week, emergency call back service.

    - Certifications: ICU/CCU entrances shall be UL listed and certified as an effective barrier for limiting the passage of smoke in accordance with UL1784 and NFPA 105.

    - Source Limitations:  Obtain ICU/CCU entrances through one source from a single manufacturer.

    - Product Options:  Drawings indicate sizes, profiles, and dimensional requirements of ICU/CCU entrances and are based on the specific system indicated.  Refer to Division 1 Section "Product Requirements."

  - PROJECT CONDITIONS

    - Field Measurements:  General Contractor shall verify openings to receive ICU/CCU entrances by field measurements before fabrication and indicate measurements on Shop Drawings.

    - Mounting Surfaces: General Contractor shall verify all surfaces to be plumb, straight and secure; substrates to be of proper dimension and material.

    - Other trades:  General Contract shall advise of any inadequate conditions or equipment.

  - COORDINATION

    - Templates:  Check Shop Drawings of other work to confirm that adequate provisions are made for locating and installing ICU/CCU entrances to comply with indicated requirements.

    - Electrical System Roughing-in: Coordinate layout and installation of ICU/CCU entrances with connections to facility grounding system.

  - WARRANTY

    - ICU/CCU entrances shall be free of defects in material and workmanship for a period of one (1) year from the date of substantial completion.

    - During the warranty period the Owner shall engage a factory-trained technician to perform service and affect repairs. A safety inspection shall be performed after each adjustment or repair and a completed inspection form shall be submitted to the Owner.

    - During the warranty period all warranty work, including but not limited to emergency service, shall be performed during normal working hours.

- PRODUCTS

  - ICU/CCU ENTRANCES

    - Manufacturer: Stanley Access Technologies; Dura-Care™ Series 7400 manual swinging ICU/CCU entrances.

  - MATERIALS

    - Aluminum:  Alloy and temper recommended by manufacturer for type of use and finish indicated.

      - Headers, stiles, rails, and frames 6063-T6

      - Extruded Bars, Rods, Profiles, and Tubes:  ASTM B 221.

      - Sheet and Plate:  ASTM B 209.

    - Sealants and Joint Fillers:  Performed under Division 7 Section "Joint Sealants".

  - ICU/CCU ENTRANCE ASSEMBLIES

    - Provide manufacturer's standard ICU/CCU entrance assemblies including doors, framing, headers, pivots, and accessories required for a complete installation.

    - ICU/CCU Entrances:

      - Configuration:

        - Simultaneous pairs.

        - Simultaneous pairs, uneven.

        - Single door.

      - Traffic Pattern:  Two-way.

      - Breakaway Capability: All active swinging panels.

      - Mounting:  Between jambs

  - COMPONENTS

    - Framing Members:  Manufacturer's standard extruded aluminum reinforced as required to support imposed loads.

      - Nominal Size: 1 ¾ inch by 4 ½ inch (44 by 115 mm).

      - Concealed Fastening: Framing shall incorporate a concealed fastening pocket, and continuous flush insert cover, extending full length of each framing member.

    - Stile and Rail Doors and Sidelights:  Manufacturer's standard 1 ¾ inch (45 mm) thick glazed doors with extruded-aluminum tubular stile and rail members. Incorporate concealed tie-rods that span full length of top and bottom rails.

      - Glazing Stops and Gaskets:  Snap-on, extruded-security aluminum stops and preformed gaskets.

      - Stile Design: Narrow stile; 2 inch (51 mm) nominal width.

      - Bottom Rail Design: Minimum 4 inch (102 mm) nominal height.

      - Muntin Bars: Horizontal tubular rail member for each door; 2 inch (51 mm) nominal height.

    - Glazing: Furnished under Division 8 Section Glazing. All Glazing furnished under separate section shall be 1/4 inch (6 mm) tempered.

    - Fasteners and Accessories:  Manufacturer's standard corrosion-resistant, non-staining, non-bleeding fasteners and accessories compatible with adjacent materials.

  - HARDWARE

    - Provide units in sizes and types recommended by ICU/CCU entrance and hardware manufacturers for entrances and uses indicated.

    - Breakaway: Provide release hardware that allows panel(s) to swing out in direction of egress to full 90 degrees. Maximum force to open panel shall be 50 lbf (222 N) with panel retaining latches released.  Limit arms shall be provided to control swing of panels on break-out; swing shall not exceed 90 degrees.

    - Continuous Hinge: Provide geared continuous hinges for swinging panels. Hinge shall be tested and approved by BHMA for ANSI A156.26-1996 Grade 1 and shall be non-handed.

    - Concealed In-Door Closer: Manufacturer’s standard units tested and certified to ANSI/BHMA A156.4, Grade 1. Size closers in accordance with manufacturer’s recommendation for door size and conditions. Closers shall incorporate the following:

      - Separate adjusting valves for closing and latching speed, and back-check.

      - Adjustable hold-open position.

    - Positive Latch:  Manufacturer's standard non-keyed, spring loaded, latch and strike that can secure swinging door panels to head, adjacent panels, or jambs. Latch shall engage by closing action of door. On single doors strike shall mount flush to surface of framing.

      - Active panels: Positive latch shall be vertical rod type, top only.

      - In-Active Panels: Semi-automatic; self latching.

    - Sliding Weather Stripping: Manufacturer's standard replaceable smoke rated components complying with AAMA 701.

    - Weather Sweeps: Manufacture’s standard dual row nylon brush sweep mounted to underside of door bottom

  - FABRICATION

    - Factory fabricate ICU/CCU entrance components to designs, sizes, and thickness indicated and to comply with indicated standards.

      - Form aluminum shapes before finishing.

      - Use concealed fasteners to greatest extent possible.

        - Where fasteners are subject to loosening or turning out from thermal and structural movements, wind loads, or vibration, use self-locking devices.

        - Reinforce members as required to receive fastener threads.

    - Framing:  Provide ICU/CCU entrances as prefabricated assemblies.

      - Fabricate tubular and channel frame assemblies with manufacturer's standard mechanical or welded joints.  Provide sub-frames and reinforcement as required for a complete system to support required loads.

      - Perform fabrication operations in manner that prevents damage to exposed finish surfaces.

      - Form profiles that are sharp, straight, and free of defects or deformations.

      - Prepare components to receive concealed fasteners and anchor and connection devices.

      - Fabricate components with accurately fitted joints with ends coped or mitered to produce hairline joints free of burrs and distortion.

    - Doors:  Factory fabricated and assembled in profiles indicated. Reinforce as required to support imposed loads and for installing hardware.

    - Glazing:  Fabricate framing with minimum glazing edge clearances for thickness and type of glazing indicated.

    - Hardware:  Factory install hardware to the greatest extent possible; remove only as required for final finishing operation and for delivery to and installation at Project site.

  - ALUMINUM FINISHES

    - Comply with NAAMM Metal Finishes Manual for Architectural and Metal Products for recommendations for applying and designing finishes. Finish designations prefixed by AA comply with system established by Aluminum Association for designing finishes.

    - Class II, Clear Anodic Finish: AA-M10C22A31 Mechanical Finish: as fabricated; Chemical Finish: etched, medium matte; Anodic Coating: Architectural Class II, clear coating 0.40 mils minimum complying with AAMA 611-98, and the following:

      - AAMA 607.1

      - Applicator must be fully compliant with all applicable environmental regulations and permits, including wastewater and heavy metal discharge.

- EXECUTION

  - INSPECTION

    - Examine conditions for compliance with requirements for installation tolerances, header support, and other conditions affecting performance of ICU/CCU entrances. Proceed with installation only after unsatisfactory conditions have been corrected.

  - INSTALLATION

    - Do not install damaged components.  Fit frame joints to produce joints free of burrs and distortion. Rigidly secure non-movement joints.

    - Entrances:  Install ICU/CCU entrances plumb and true in alignment with established lines and grades without warp or rack of framing members and doors.  Anchor securely in place.

      - Install surface-mounted hardware using concealed fasteners to greatest extent possible.

      - Set headers, carrier assemblies, tracks, operating brackets, and guides level and true to location with anchorage for permanent support.

    - Grounding:  Connect ICU/CCU entrances to building grounding system as specified in Division 26 Sections.

    - Glazing: Performed under Division 8 Section "Glazing" in accordance with ICU/CCU entrance manufacture’s instructions.

    - Sealants:  Comply with requirements specified in Division7 Section "Joint Sealants".

  - FIELD QUALITY CONTROL

    - Testing Services:  Factory Trained Installer shall test and inspect each ICU/CCU entrance to determine compliance of installed systems with applicable standards.

  - ADJUSTING

    - Adjust ICU/CCU entrances, and hardware for smooth and safe operation.

  - CLEANING AND PROTECTION

    - Clean glass and aluminum surfaces promptly after installation.  Remove excess glazing and sealant compounds, dirt, and other substances.  Repair damaged finish to match original finish. Comply with requirements in Division 8 Section “Glazing”, for cleaning and maintaining glass.

END OF SECTION 08 42 43

Available options not specified in this document are summarized as follows:

Configuration Options: (All Specified)

Simultaneous Pair

Simultaneous Pair, Uneven

Single Door

Header options:

1 3/4 inch (44 mm) height  (Specified)

4 inch (102 mm) height.

Finish (Class 2, Clear Anodized specified) options include:

Standard color anodizing options.

Multi-coat Fluoropolymer painted finishes.

Cladding.

Stile options;

Narrow stile 2 inch (51 mm) (Specified)

Medium stile 3 ½ inch (89 mm) available

Bottom rail options; up to 18 inch (457 mm).

Glazing options to 1 inch (25 mm) thick; supporting installation of “mini-blinds”.

Smoke & Draft control system (Specified)

Anti-Microbial coating of “Touch Points” or full package.

Contact SpecCentre services or your local Stanley Access Technologies representative for more information on specifying the right sliding automatic entrance for your project.

These specifications represent a “sample” door configuration and depict design features that are commonly used. These specifications do not reflect “standard” features and are provided for informational purposes only. Please note that there is no standard “off the shelf” product.  Stanley custom manufactures each product to its customers’ specifications. It is the customer’s responsibility to validate that a particular configuration of Stanley’s products is suitable for a specific application.  All specifications and designs contained herein are subject to change without notice or obligation.